## Elevated Tank (RTU2)
JOB# | 56276 | Desc: . – Tank
RTU101D-Cellular Digi Cat1 | RTU 2
Elevated TANK
Variable Description |  | Type | Scale | Units | Address | Origin
Physical
Digital Inputs | Location | Type | Scale | Units
Power_Failure | Din1 | Digital | T/F |  | 10001 | Local
Lead_Well_Call | Din2 | Digital | T/F |  | 10002 | Local
Lag_Well_Call | Din3 | Digital | T/F |  | 10003 | Local
Tank_Low_Level | Din4 | Digital | T/F |  | 10004 | Local
Tank_High_Level | Din5 | Digital | T/F |  | 10005 | Local
Spare | Din6 | Digital | T/F |  | 10006 | Local
Spare | Din7 | Digital | T/F |  | 10007 | Local
Spare | Din8 | Digital | T/F |  | 10008 | Local
Battery_OK | Din9 | Digital | T/F |  | 10008 | Local
Analog Inputs | Location | Type | Scale | Units
Tank_Level | Ain1 | Analog | 0-35 | ft | 30001
Spare | Ain2 | Analog | 0-??/ |  | 30002
Analog Outputs | Location | Type | Scale | Units
Spare | Aout1 | Analog | 0-??? |  | 40001
Spare | Aout2 | Analog | 0-??? |  | 40002
Digital Outputs | Location | Type | Scale | Units
Spare | Dout1 | Digital | T/F |  | 20001
Spare | Dout2 | Digital | T/F |  | 20002
Spare | Dout3 | Digital | T/F |  | 20003
Spare | Dout4 | Digital | T/F |  | 20004
Subscribe Topics | Notes
56264/RTU/1/SETPOINTS | The tank will receive the well stop and start level setpoints from VTS. All the system setpoints will be published with one topic in the form: Street_Dept_Well_Stop_Setpoint,Street_Dept_Well_Start_Setpoint,Hiway_61_Well_Stop_Setpoint,Hiway_61__Well_Start_Setpoint. All setpoints will be multiplied by 10, so 25.4 becomes 254.
56264/RTU/1/FORCES | The tank will receive the well forces from VTS. All system forces will be published with one topic in the form:Street_Dept_Well_Force_On,Street_Dept_Well_Force_Off,Hiway_61_Well_Force_On,Hiway_61_Well_Force_Off.
Publish Topics
56264/RTU/2/DI_STATUS | Publish all DI
56264/RTU/2/AI_STATUS | Publish all AI

## Well #1 (RTU3)
JOB# | 56276 | Desc: . – Well #1
RTU101D-Cellular Digi Cat1 | RTU 3
WELL #1
Variable Description |  | Type | Scale | Units | Address
Physical
Digital Inputs | Location | Type | Scale | Units
Power_Failure | Din1 | Digital | T/F |  | 10001
Well_1_Failure | Din2 | Digital | T/F |  | 10002
Well_2_Failure | Din3 | Digital | T/F |  | 10003
Spare | Din4 | Digital | T/F |  | 10004
Spare | Din5 | Digital | T/F |  | 10005
Spare | Din6 | Digital | T/F |  | 10006
Spare | Din7 | Digital | T/F |  | 10007
Spare | Din8 | Digital | T/F |  | 10008
Battery_OK | Din9 | Digital | T/F |  | 10008 | Local
Analog Inputs | Location | Type | Scale | Units
Spare | Ain1 | Analog | 0-35 | ft | 30001
Spare | Ain2 | Analog | 0-??? |  | 30002
Analog Outputs | Location | Type | Scale | Units
Spare | Aout1 | Analog | 0-??? |  | 40001
Spare | Aout2 | Analog | 0-??? |  | 40002
Digital Outputs | Location | Type | Scale | Units
Lead_Well_Call | Dout1 | Digital | T/F |  | 00001
Lag_Well_Call | Dout2 | Digital | T/F |  | 00002
Tank_Low_Level | Dout3 | Digital | T/F |  | 00003
Tank_High_Level | Dout4 | Digital | T/F |  | 00004
Subscribe Topics | Notes
56264/RTU/1/SETPOINTS | The tank will receive the well stop and start level setpoints from VTS. All the system setpoints will be published with one topic in the form: Street_Dept_Well_Stop_Setpoint,Street_Dept_Well_Start_Setpoint,Hiway_61_Well_Stop_Setpoint,Hiway_61__Well_Start_Setpoint. All setpoints will be multiplied by 10, so 25.4 becomes 254.
56264/RTU/1/FORCES | The tank will receive the well forces from VTS. All system forces will be published with one topic in the form:Street_Dept_Well_Force_On,Street_Dept_Well_Force_Off,Hiway_61_Well_Force_On,Hiway_61_Well_Force_Off.
Publish Topics
56264/RTU/2/DI_STATUS | Publish all DI
56264/RTU/2/AI_STATUS | Publish all AI