## CTU (RTU1)
JOB# | 56264 | Desc: . – CTU
Modbus Server via Internet | CTU
Variable Description |  | Type | Scale | Units | Address | Origin | Destination
Digital Inputs |  | Type | Scale | Units
Power_Failure |  | Digital | T/F |  | 10201 | RTU 2 | VTS
Well_Running |  | Digital | T/F |  | 10202 | RTU 2 | VTS
Well_Failure |  | Digital | T/F |  | 10203 | RTU 2 | VTS
Spare |  | Digital | T/F |  | 10204 | RTU 2 | VTS
Spare |  | Digital | T/F |  | 10205 | RTU 2 | VTS
Spare |  | Digital | T/F |  | 10206 | RTU 2 | VTS
Spare |  | Digital | T/F |  | 10207 | RTU 2 | VTS
Spare |  | Digital | T/F |  | 10208 | RTU 2 | VTS
Battery_OK |  | Digital | T/F |  | 10209 | RTU 3 | VTS
Well_Force_On |  | Digital | T/F |  | 10210 | RTU 4 | VTS
Well_Force_Off |  | Digital | T/F |  | 10211 | RTU 5 | VTS
Power_Failure |  | Digital | T/F |  | 10301 | RTU 3 | VTS
Well_Running |  | Digital | T/F |  | 10302 | RTU 3 | VTS
Well_Failure |  | Digital | T/F |  | 10303 | RTU 3 | VTS
Spare |  | Digital | T/F |  | 10304 | RTU 3 | VTS
Spare |  | Digital | T/F |  | 10305 | RTU 3 | VTS
Spare |  | Digital | T/F |  | 10306 | RTU 3 | VTS
Spare |  | Digital | T/F |  | 10307 | RTU 3 | VTS
Spare |  | Digital | T/F |  | 10308 | RTU 3 | VTS
Battery_OK |  | Digital | T/F |  | 10309 | RTU 4 | VTS
Well_Force_On |  | Digital | T/F |  | 10310 | RTU 5 | VTS
Well_Force_Off |  | Digital | T/F |  | 10311 | RTU 6 | VTS
Power_Failure |  | Digital | T/F |  | 10401 | RTU4 | VTS
High Water |  | Digital | T/F |  | 10402 | RTU4 | VTS
Pump_1_Running |  | Digital | T/F |  | 10403 | RTU4 | VTS
Pump_2_Running |  | Digital | T/F |  | 10404 | RTU4 | VTS
Pump_3_Running |  | Digital | T/F |  | 10405 | RTU4 | VTS
Pump_1_Failure |  | Digital | T/F |  | 10406 | RTU4 | VTS
Pump_2_Failure |  | Digital | T/F |  | 10407 | RTU4 | VTS
Pump_3_Failure |  | Digital | T/F |  | 10408 | RTU4 | VTS
Power_Failure |  | Digital | T/F |  | 10501 | RTU5 | VTS
High Water |  | Digital | T/F |  | 10502 | RTU6 | VTS
Pump_1_Running |  | Digital | T/F |  | 10503 | RTU7 | VTS
Pump_2_Running |  | Digital | T/F |  | 10504 | RTU8 | VTS
Pump_1_Failure |  | Digital | T/F |  | 10505 | RTU9 | VTS
Pump_2_Failure |  | Digital | T/F |  | 10506 | RTU10 | VTS
Spare |  | Digital | T/F |  | 10507 | RTU11 | VTS
Spare |  | Digital | T/F |  | 10508 | RTU12 | VTS
RTU 2 Comm Failure |  | Digital | T/F |  | 10001 | AWS | VTS
RTU 3 Comm Failure |  | Digital | T/F |  | 10002 | AWS | VTS
RTU 4 Comm Failure |  | Digital | T/F |  | 10003 | AWS | VTS
RTU 5 Comm Failure |  | Digital | T/F |  | 10003 | AWS | VTS
Analog Inputs |  | Type | Scale | Units
Tank_Level |  | Analog | 0-35 | ft | 30201 | RTU2 | VTS
Spare |  | Analog | 0-??? |  | 30202 | RTU2 | VTS
Tank_Level |  | Analog | 0-35 | ft | 30301 | RTU3 | VTS
Spare |  | Analog | 0-??? |  | 30302 | RTU3 | VTS
Spare |  | Analog | 0-??? |  | 30401 | RTU4 | VTS
Spare |  | Analog | 0-??? |  | 30402 | RTU4 | VTS
Spare |  | Analog | 0-??? |  | 30501 | RTU5 | VTS
Spare |  | Analog | 0-??? |  | 30502 | RTU5 | VTS
Analog Outputs |  | Type | Scale | Units
Street_Dept_Well_Stop_Setpoint |  | Analog | 0-350 | ft. * 10 | 40001 | VTS | RTU2
Street_Dept_Well_Start_Setpoint |  | Analog | 0-350 | ft. * 10 | 40002 | VTS | RTU2
Hiway_61_Well_Stop_Setpoint |  | Analog | 0-350 | ft. * 10 | 40003 | VTS | RTU3
Hiway_61__Well_Start_Setpoint |  | Analog | 0-350 | ft. * 10 | 40004 | VTS | RTU3
Digital Outputs |  | Type | Scale | Units
Street_Dept_Well_Force_On |  | Digital | T/F |  | 00001 | VTS | RTU 2
Hiway_61_Well_Force_On |  | Digital | T/F |  | 00002 | VTS | RTU 3

## Street Dept (RTU2)
JOB# | 56264 | Desc: . – Tank/Well
RTU101D-Cellular Digi Cat1 | RTU 2
STREET DEPARTMENT TANK/WELL
Variable Description |  | Type | Scale | Units | Address | Origin
Physical
Digital Inputs | Location | Type | Scale | Units
Power_Failure | Din1 | Digital | T/F |  | 10001 | Local
Well_Running | Din2 | Digital | T/F |  | 10002 | Local
Well_Failure | Din3 | Digital | T/F |  | 10003 | Local
Spare | Din4 | Digital | T/F |  | 10004 | Local
Spare | Din5 | Digital | T/F |  | 10005 | Local
Spare | Din6 | Digital | T/F |  | 10006 | Local
Spare | Din7 | Digital | T/F |  | 10007 | Local
Spare | Din8 | Digital | T/F |  | 10008 | Local
Battery_OK | Din9 | Digital | T/F |  | 10008 | Local
Well_Force_On | Din10 | Digital | T/F |  | 10008 | VTS
Well_Force_Off | Din11 | Digital | T/F |  | 10008 | VTS
Analog Inputs | Location | Type | Scale | Units
Tank_Level | Ain1 | Analog | 0-35 | ft | 30001
Spare | Ain2 | Analog | 0-??/ |  | 30002
Well_Stop_Setpoint | Ain3 | Analog | 0-35 | ft. * 10 | 30003
Well_Start_Setpoint | Ain4 | Analog | 0-35 | ft. * 10 | 30004
Analog Outputs | Location | Type | Scale | Units
Spare | Aout1 | Analog | 0-??? |  | 40001
Spare | Aout2 | Analog | 0-??? |  | 40002
Well_Stop_Setpoint | Aout3 | Analog | 0-35 | ft. * 10 | 40003 | VTS
Well_Start_Setpoint | Aout4 | Analog | 0-35 | ft. * 10 | 40004 | VTS
Digital Outputs | Location | Type | Scale | Units
Well_Run | Dout1 | Digital | T/F |  | 00001
Spare | Dout2 | Digital | T/F |  | 00002
Spare | Dout3 | Digital | T/F |  | 00003
Spare | Dout4 | Digital | T/F |  | 00004
Well_Force_On | Dout5 | Digital | T/F |  | 00005
Well_Force_Off | Dout6 | Digital | T/F |  | 00006
Subscribe Topics | Notes
56264/RTU/1/SETPOINTS | The tank will receive the well stop and start level setpoints from VTS. All the system setpoints will be published with one topic in the form: Street_Dept_Well_Stop_Setpoint,Street_Dept_Well_Start_Setpoint,Hiway_61_Well_Stop_Setpoint,Hiway_61__Well_Start_Setpoint. All setpoints will be multiplied by 10, so 25.4 becomes 254.
56264/RTU/1/FORCES | The tank will receive the well forces from VTS. All system forces will be published with one topic in the form:Street_Dept_Well_Force_On,Street_Dept_Well_Force_Off,Hiway_61_Well_Force_On,Hiway_61_Well_Force_Off.
Publish Topics
56264/RTU/2/DI_STATUS | Publish all DI
56264/RTU/2/AI_STATUS | Publish all AI

## Hiway 61 (RTU3)
JOB# | 56264 | Desc: . – Tank/Well
RTU101D-Cellular Digi Cat1 | RTU 3
HIWAY 61 TANK/WELL
Variable Description |  | Type | Scale | Units | Address
Physical
Digital Inputs | Location | Type | Scale | Units
Power_Failure | Din1 | Digital | T/F |  | 10001
Well_Running | Din2 | Digital | T/F |  | 10002
Well_Failure | Din3 | Digital | T/F |  | 10003
Spare | Din4 | Digital | T/F |  | 10004
Spare | Din5 | Digital | T/F |  | 10005
Spare | Din6 | Digital | T/F |  | 10006
Spare | Din7 | Digital | T/F |  | 10007
Spare | Din8 | Digital | T/F |  | 10008
Battery_OK | Din9 | Digital | T/F |  | 10008 | Local
Well_Force_On | Din10 | Digital | T/F |  | 10008 | VTS
Well_Force_Off | Din11 | Digital | T/F |  | 10008 | VTS
Analog Inputs | Location | Type | Scale | Units
Tank_Level | Ain1 | Analog | 0-35 | ft | 30001
Spare | Ain2 | Analog | 0-??? |  | 30002
Well_Stop_Setpoint | Ain3 | Analog | 0-350 | ft. * 10 | 30003
Well_Start_Setpoint | Ain4 | Analog | 0-350 | ft. * 10 | 30004
Analog Outputs | Location | Type | Scale | Units
Spare | Aout1 | Analog | 0-??? |  | 40001
Spare | Aout2 | Analog | 0-??? |  | 40002
Well_Stop_Setpoint | Aout3 | Analog | 0-350 | ft. * 10 | 40003 | VTS
Well_Start_Setpoint | Aout4 | Analog | 0-350 | ft. * 10 | 40004 | VTS
Digital Outputs | Location | Type | Scale | Units
Well_Run | Dout1 | Digital | T/F |  | 00001
Spare | Dout2 | Digital | T/F |  | 00002
Spare | Dout3 | Digital | T/F |  | 00003
Spare | Dout4 | Digital | T/F |  | 00004
Well_Force_On | Dout5 | Digital | T/F |  | 00005
Well_Force_Off | Dout6 | Digital | T/F |  | 00006
Subscribe Topics | Notes
56264/RTU/1/SETPOINTS | The tank will receive the well stop and start level setpoints from VTS. All the system setpoints will be published with one topic in the form: Street_Dept_Well_Stop_Setpoint,Street_Dept_Well_Start_Setpoint,Hiway_61_Well_Stop_Setpoint,Hiway_61__Well_Start_Setpoint. All setpoints will be multiplied by 10, so 25.4 becomes 254.
56264/RTU/1/FORCES | The tank will receive the well forces from VTS. All system forces will be published with one topic in the form:Street_Dept_Well_Force_On,Street_Dept_Well_Force_Off,Hiway_61_Well_Force_On,Hiway_61_Well_Force_Off.
Publish Topics
56264/RTU/2/DI_STATUS | Publish all DI
56264/RTU/2/AI_STATUS | Publish all AI

## Racquet Club(RTU4)
JOB# | 56264 | Desc: . – Triplex Liftstation
RTU101D-Cellular Digi Cat1 | RTU 4
WELL 3
Variable Description |  | Type | Scale | Units | Address
Physical
Digital Inputs | Location | Type | Scale | Units
Power_Failure | Din1 | Digital | T/F |  | 10001
High_Water | Din2 | Digital | T/F |  | 10002
Pump_1_Running | Din3 | Digital | T/F |  | 10003
Pump_2_Running | Din4 | Digital | T/F |  | 10004
Pump_3_Running | Din5 | Digital | T/F |  | 10005
Pump_1_Failure | Din6 | Digital | T/F |  | 10006
Pump_2_Failure | Din7 | Digital | T/F |  | 10007
Pump_3_Failure | Din8 | Digital | T/F |  | 10008
Analog Inputs | Location | Type | Scale | Units
Spare | Ain1 | Analog | 0-??? |  | 30001
Spare | Ain2 | Analog | 0-??? |  | 30002
Spare | Ain3 | Analog | 0-??? |  | 30003
Spare | Ain4 | Analog | 0-??? |  | 30004
Analog Outputs | Location | Type | Scale | Units
Spare | Aout1 | Analog | 0-??? |  | 40001
Spare | Aout2 | Analog | 0-??? |  | 40002
Digital Outputs | Location | Type | Scale | Units
Spare | Dout1 | Digital | T/F |  | 00001
Spare | Dout2 | Digital | T/F |  | 00002
Spare | Dout3 | Digital | T/F |  | 00003
Spare | Dout4 | Digital | T/F |  | 00004

## Fire Station(RTU5)
JOB# | 56264 | Desc: . – Duplex Lift Station
RTU101D-Cellular Digi Cat1 | RTU 5
WELL 3
Variable Description |  | Type | Scale | Units | Address
Physical
Digital Inputs | Location | Type | Scale | Units
Power_Failure | Din1 | Digital | T/F |  | 10001
High_Water | Din2 | Digital | T/F |  | 10002
Pump_1_Running | Din3 | Digital | T/F |  | 10003
Pump_2_Running | Din4 | Digital | T/F |  | 10004
Pump_1_Failure | Din5 | Digital | T/F |  | 10005
Pump_2_Failure | Din6 | Digital | T/F |  | 10006
Spare | Din7 | Digital | T/F |  | 10007
Spare | Din8 | Digital | T/F |  | 10008
Analog Inputs | Location | Type | Scale | Units
Spare | Ain1 | Analog | 0-??? |  | 30001
Spare | Ain2 | Analog | 0-??? |  | 30002
Spare | Ain3 | Analog | 0-??? |  | 30003
Spare | Ain4 | Analog | 0-??? |  | 30004
Analog Outputs | Location | Type | Scale | Units
Spare | Aout1 | Analog | 0-??? |  | 40001
Spare | Aout2 | Analog | 0-??? |  | 40002
Digital Outputs | Location | Type | Scale | Units
Spare | Dout1 | Digital | T/F |  | 00001
Spare | Dout2 | Digital | T/F |  | 00002
Spare | Dout3 | Digital | T/F |  | 00003
Spare | Dout4 | Digital | T/F |  | 00004